NOT APPROVED - CORRECTION NOTICE

City of Los Angeles Department of Building and Safety

| JOB ADDRESS: 520 W MANCHESTER AVE |  |  | PERMIT #: 15041-10000-24894 |  |
| --- | --- | --- | --- | --- |
| JOB DESCRIPTION: Electrical |  |  | FOR REINSPECTION CALL: (888)LA4-BUILD or 311 INSPECTOR: WILFRED LOMELI DISTRICT: EGIM4 PHONE: (213) 202-3134 BUREAU: Inspection Bureau DATE: 8/7/2017 |  |
| APPLICANT/AGENT: MIRON ELECTRIC CONSTRUCTION CORP |  |  |  |  |
| ADDRESS: 9238 DEERING AVE |  |  |  |  |
| CITY: CHATSWORTH | STATE: CA | ZIPCODE: 91311 |  |  |
| Before the work or installation authorized by this permit can be approved, concealed, energized, or used, the following deficiencies shall be corrected. Call for reinspection when all corrections have been made. |  |  |  |  |
| PERMIT GROUP/TYPE/SUBTYPE: Electrical/Electrical/Commercial |  |  |  |  |
| VIOLATION NUMBER: 17SQJ02528 Date Issued: 8/6/2017 Issued by INSPECTION TYPE: Rough VIOLATION TYPE: Installation and use. VIOLATION CODE SECTION: 93.110.3 (A) and (B) LAMC CODE LANGUAGE: Listed or labeled equipment shall be installed in accordance with any instructions included on the listing or labeling. VIOLATION NOTES: Removable covers meant to allow access to the generator shall not be blocked or render non removable by other equipment. |  |  |  |  |
| VIOLATION NUMBER: 17SQJ02529 Date Issued: 8/6/2017 Issued by INSPECTION TYPE: Rough VIOLATION TYPE: MCC overcurrent protection. VIOLATION CODE SECTION: 93.430.94 LAMC CODE LANGUAGE: Motor control centers shall be provided with overcurrent protection in accordance with parts I, II, and VIII of Article 240. This protection shall be provided by an overcurrent protecting device ahead of the MCC or located within the MCC VIOLATION NOTES: Provide the required overcurrent protection for the MCC. |  |  |  |  |

INSP/Form. 49e (1/11/2006)

Information generated from mPower

DO NOT REMOVE THIS NOTICE

http://ladbs.org

Attachment 22.2-3

Page 1 of 1

Page 1 of 1